## Slide 1
Germany PCM Case Build
From raw public data to consistent nodal and zonal HOPE cases
Core design rule
Build one nodal master case first, then derive the zonal case mechanically.
Nodal Buses
783
Nodal Lines
1174
Generators
4267
Demo Cost
$226.37M
Network backbone: OSM Europe transmission dataset + PyPSA-Eur reference workflow
Fleet: powerplantmatching with Germany-specific validation layers
Chronology: SMARD national load + generation and four TSO load helper files

## Slide 2
Executive Summary
How the Germany case was assembled and why the design is comparison-friendly
Goal
Create one canonical Germany PCM dataset that supports both nodal and zonal analysis.
Method
Freeze every major mapping once: generator -> bus -> zone -> zonal derivative.
Outcome
A solved 2-day nodal demo case plus a consistent 4-zone zonal comparison case.

## Slide 3
Source Stack
Each layer was chosen to keep the zonal case derived from, not detached from, the nodal case
Network
OSM Europe transmission dataset
PyPSA-Eur workflow reference
Fleet
powerplantmatching
BNetzA validation support
Chronology
SMARD Germany load + generation
SMARD TSO load helper files
Map Geometry
Germany state boundary GeoJSON
reconstructed 4-TSO overlay

## Slide 4
Integration Architecture
The zonal case is produced by aggregation from the nodal master case
Raw Sources
Cleaned Staging
Frozen Maps
Nodal Master
Zonal Derivative
Network cleaner produces stable buses, lines, transformers, and links.
Fleet cleaner assigns each generator to one nodal bus and inherits one zone tag.
Chronology builder freezes one 2025 hourly basis and optional zonal load shares.
Zonal seams and capacities are derived from the nodal cross-zone structure.

## Slide 5
Build Steps
Six steps turned raw public data into the Germany PCM comparison set
1
Network backbone
Normalize OSM Europe inputs and keep a connected 783-bus Germany network.
2
Bus-zone mapping
Freeze one Bus_id -> TSO zone table for 50Hertz, Amprion, TenneT, and TransnetBW.
3
Generator mapping
Clean powerplantmatching and assign each plant to a nodal bus once.
4
Chronology
Build one 2025 hourly chronology with 8760 rows and reuse it everywhere.
5
Case assembly
Build the canonical nodal case first and aggregate the zonal case from it.
6
Dashboard geometry
Reconstruct a file-backed Germany TSO overlay from state boundaries and frozen bus geography.

## Slide 6
Case Snapshot
Current master and derivative cases in the repo
Nodal Master Case
Zonal Derivative Case
783 buses
1174 lines
4267 generator entries
8760-hour canonical chronology
4 zones
5 interzonal interfaces
70 zonal generator entries
Derived from nodal geography and seams
Design choice: the zonal case is not independently calibrated; it is aggregated from the nodal master dataset.

## Slide 7
Assumptions And Caveats
Important choices to explain when comparing Germany nodal and zonal results
Frozen Modeling Choices
Current Caveats
Use one nodal master case as the canonical truth source.
Use four TSO research zones instead of the real DE-LU bidding zone.
Keep representative-day modes off for PCM debug validation windows.
Preserve chronology consistency before adding more model complexity.
The Germany TSO dashboard overlay is reconstructed, not official GIS.
The 2-day nodal demo case is solve-proven; longer nodal horizons still need staged validation.
Generator validation against MaStR and Kraftwerksliste can still be deepened.
Historical benchmarking should keep expanding as the case matures.

## Slide 8
Debugging Journey
The nodal case became usable after fixing topology and electrical scaling
Initial failure
Disconnected components, singular-network behavior, and severe angle-limit pathologies.
Core fixes
Transformer connectivity, largest connected component, and HOPE-scale reactance normalization.
Usable result
A 1-day and then 2-day full-nodal Germany debug run solved cleanly with zero load shedding.

## Slide 9
Solved Demo Outcome
2-day January nodal case used for the current Germany dashboard demo
Solve Window
48 hours
Total Cost
$226.37M
Load Shedding
0.0
Dashboard Status
Default case
Chart: Operating cost by zone
| 50Hertz | Amprion | TenneT | TransnetBW
Operating cost ($M) | 62.0774 | 94.1478 | 35.2161 | 34.9272
Why this matters
The solved 2-day nodal case is stable enough to demo the Germany dashboard while the longer nodal horizon is still being staged.

## Slide 10
Next Steps
What to improve next in the Germany case build
Data QA
Deepen plant validation and benchmark chronology totals against SMARD.
Nodal Scale-Up
Extend from short-window nodal success toward longer production horizons.
Geometry
Swap the reconstructed TSO overlay for official GIS if a public layer appears.
Storytelling
Compare nodal and zonal outputs directly in the dashboard and in papers.

## Slide 11
Key Files In The Repo
Useful paths for updating the Germany build and the dashboard story
Build workspace
E:/MIT Dropbox/Shen Wang/MIT/RA/HOPE_project/ModelCases/tools/germany_pcm_case_related
Dashboard geometry
E:/MIT Dropbox/Shen Wang/MIT/RA/HOPE_project/tools/hope_dashboard/data/germany_tso_zones.geojson
Nodal master case
E:/MIT Dropbox/Shen Wang/MIT/RA/HOPE_project/ModelCases/GERMANY_PCM_nodal_case
Zonal derivative case
E:/MIT Dropbox/Shen Wang/MIT/RA/HOPE_project/ModelCases/GERMANY_PCM_zonal4_case